## Register Map
SECTION 1: STATUS | CERV FUNCTION BYTE = 0x00
Parameter Name | Register # | # Bytes | Range | Scale | Measurement Interval | Description
TFROMIN | 1 | 1 | 0-255 | {0,255} = {-50, 205} F | 10s | Temperature From Inside (Return Air)
TFROMOUT | 3 | 1 | 0-255 | {0,255} = {-50, 205} F | 10s | Temperature From Outside (Fresh Air)
RHFROMIN | 5 | 1 | 0-100 | % | 10s | Relative Humidity From Inside (Return Air)
RHFROMOUT | 6 | 1 | 0-100 | % | 10s | Relative Humidity From Outside (Fresh Air)
CO2 | 7 | 2 | 400 - 5000 | ppm | 10s | Indoor (return air) CO2 PPM
VOC | 8 | 2 | 400 - 5000 | ppm | 10s | Indoor (return air) VOC PPM
FANINSPEED | 11 | 1 | 0-100 | % | - | Current Supply Fan Speed
FANOUTSPEED | 12 | 1 | 0-100 | % | - | Current Exhaust Fan Speed
MODESTATUS | 13 | 1 | 0-11 | 0 = recirc-cool, 1 = vent-cool, 2 = free-cool, 3 = recirc-heat, 4 = vent-heat, 5 = free-heat, 6 = vent setpoint, 7 = off, 8 = Assess, 11 = Recirculation | - | Current CERV Mode Indicator
HEATCOOL | 14 | 1 | 0-1 | 0 = Cool, 1 = Heat | - | Reversing Valve positon
VENTRECIRC | 15 | 1 | 0-1 | 0 = Ventilation, 2 = Recirculation | - | Inlet Damper position
FORCEVENTTIME | 16 | 1 | 0-255 | minutes | - | Time remaining for manual (touchscreen) triggered ventilation
SWITCHSTAT | 17 | 1 | 0-1 | 0 = off, 1 = on | 5s | Indicator for ventilation due to remote ventilation wall switch(es)
SECTION 2: SETTINGS | CERV FUNCTION BYTE = 0x02
HEATSETPT | 2 | 1 | 55 - CoolSetpt | F | - | Heating Setpoint (cannot set above Cooling Setpoint)
COOLSETPT | 3 | 1 | HeatSetpt - 90 | F | - | Cooling Setpoint (cannot set below Heating Setpoint)
VENTSETPT | 4 | 2 | 500-2000 | {500, 2000} ppm | - | Ventilation setpoint (scaled by 10)
CO2ENABLED | 5 | 1 | 0-1 | 0 = CO2 disabled for ventilation control 1 = CO2 enabled for ventilation control | - | Enable/Disable status for using IAQ sensors to ventilate
VOCENABLED | 6 | 1 | 0-1 | 0 = VOC disabled for ventilation control 1 = VOC enabled for ventilation control | - | Enable/Disable status for using IAQ sensors to ventilate

## Enocean Messages
NOTE: These example messages do not contain all of the data from a normal CERV transmission. There will be some additional data sent before & after the temperatures/settings that you should ignore. The main thing your process should really be: 1) Store the entire message in a buffer. 2) Check the CRC fields to make sure everything is complete and valid. 3) loop through the data portion (starting at byte 10) and grab values. It will always repeat as Register # -> Length -> Data (1 or more bytes)
EXAMPLE MESSAGE STRUCTURE - STATUS
gray cells are fields that never change
Byte #
HEADER
0 | Start | 55
1 | Data Length H | 0 | Data Length = 0x0059 = 89 bytes
2 | Data Length L | 59
3 | "Optional Data" Length | 0A | Optional data contains destination
4 | Packet Type | 7 | doesn't change
5 | CRC | 89 | CRC-8 of bytes 1-4. See https://crccalc.com/
DATA INFO HEADER
6 |  | 0
7 | CERV FUNCTION BYTE | 0 | 0x00 = STATUS, 0x02 = SETTINGS. See Register Map
8 |  | 2 | doesn't change
9 |  | 7 | doesn't change
CERV DATA
10 | Register # | 1 | 0x01 = TFROMIN
11 | Length | 1 | 0x01 = 1 Byte
12 | Value | 78 | 0x78 = 120. Subtract 50 on temperatures, so T Inside = 120-50 = 70
13 | Register # | 3 | 0x03 = TFROMOUT
14 | Length | 1 | 0x01 = 1 Byte
15 | Value | 52 | 0x52 = 82. Subtract 50 on temperatures, so T Outside = 82-50 = 32
16 | Register # | 5 | 0x05 = RHFROMIN
17 | Length | 1 | 0x01 = 1 Byte
18 | Value | 2D | 0x2D = 45. Indoor RH is 45%
19 | Register # | 6 | 0x06 = RHFROMOUT
20 | Length | 1 | 0x01 = 1 Byte
21 | Value | 19 | 0x19 = 25. Indoor RH is 25%
22 | Register # | 7 | 0x07 = CO2
23 | Length | 2 | 0x02 = 2 Bytes
24 | Value H | 1 | 0x01C2 = 450. Indoor CO2 = 450
25 | Value L | C2
26 | Register # | 8 | 0x0 = VOC
27 | Length | 2 | 0x02 = 2 Bytes
28 | Value H | 4 | 0x0433 = 1075. Indoor VOC = 1075
29 | Value L | 33
......etc….........
OPTIONAL DATA
96 | USB Module ADD[0] | xx | This will be your USB module's address.
97 | USB Module ADD[1] | xx
98 | USB Module ADD[2] | xx
99 | USB Module ADD[3] | xx
100 | Source ADD[0] | xx | The CERV's Enocean Address
101 | Source ADD[1] | xx
102 | Source ADD[2] | xx
103 | Source ADD[3] | xx
104 | dBm | xx | Signal Strength
105 | delay | 0
106 | DATA CRC | xx | CRC-8 of all DATA INFO HEADER & CERV DATA & OPTIONAL DATA (i.e. Bytes 6-105). See https://crccalc.com/
EXAMPLE MESSAGE STRUCTURE - SETTINGS
gray cells are fields that never change
Byte #
HEADER
0 | Start | 55
1 | Data Length H | 0 | Data Length = 0x005C = 92 bytes
2 | Data Length L | 5C
3 | "Optional Data" Length | 0A | Optional data contains destination
4 | Packet Type | 7 | doesn't change
5 | CRC | 49 | CRC-8 of bytes 1-4. See https://crccalc.com/
DATA INFO HEADER
6 |  | 0
7 | CERV FUNCTION BYTE | 2 | 0x00 = STATUS, 0x02 = SETTINGS. See Register Map
8 |  | 2 | doesn't change
9 |  | 7 | doesn't change
CERV DATA
10 | Register # | 2 | 0x02 = HEATSETPT
11 | Length | 1 | 0x01 = 1 Byte
12 | Value | 44 | 0x44 = 68. Heating Setpoint = 68F
13 | Register # | 3 | 0x03 = COOLSETPT
14 | Length | 1 | 0x01 = 1 Byte
15 | Value | 4C | 0x4C = 76. Cooling Setpoint = 76F
16 | Register # | 4 | 0x04 = VENTSETPT
17 | Length | 2 | 0x02 = 2 Bytes
18 | Value H | 3 | 0x03E8 = 1000. Indoor Air Quality Setpoint = 1000ppm
19 | Value L | E8
......etc….........
OPTIONAL DATA
99 | USB Module ADD[0] | xx | This will be your USB module's address.
100 | USB Module ADD[1] | xx
101 | USB Module ADD[2] | xx
102 | USB Module ADD[3] | xx
103 | Source ADD[0] | xx | The CERV's Enocean Address
104 | Source ADD[1] | xx
105 | Source ADD[2] | xx
106 | Source ADD[3] | xx
107 | dBm | xx | Signal Strength
108 | delay | 0
109 | DATA CRC | xx | CRC-8 of all DATA INFO HEADER & CERV DATA & OPTIONAL DATA (i.e. Bytes 6-108). See https://crccalc.com/